REGIONAL POWER FAILURE PREDICTION

Comprehensive ML Model Comparison Report

Weather vs. Non-Weather Model Performance Analysis

| 🔵 WITHOUT WEATHER SVM • ANN • CNN • RNN | 🟢 WITH WEATHER SVMW • CNN-W • RNNW |
| --- | --- |

Models Covered

ANN  |  CNN vs CNN-W  |  SVM vs SVMW  |  RNN vs RNNW

Uttar Pradesh Power Distribution Grid  |  Predictive Fault Classification

# 1. Executive Summary

This report consolidates findings from four separate machine learning experiments — ANN, CNN, SVM, and RNN — each trained to predict the cause or severity of electrical faults in the Uttar Pradesh power distribution grid. For CNN, SVM, and RNN, both a non-weather and a weather-enhanced variant were evaluated side by side.

Key finding across all experiments: incorporating weather features consistently improves model performance, with the CNN model showing the most dramatic uplift (+16.95 pp accuracy, macro F1 nearly tripled). The optimised SVM without weather outperforms the baseline SVMW due to superior feature engineering — demonstrating that feature quality matters as much as input breadth.

| Model | Accuracy | Macro F1 | Weighted F1 | Weather? | Winner? |
| --- | --- | --- | --- | --- | --- |
| ANN (Baseline) | 42.46% | 0.12 | 0.39 | No | — |
| SVM (Optimised) | 54.67% | 0.488 | 0.535 | No | ✓ Best No-Wx |
| SVMW (Baseline) | 41.3% | 0.28 | 0.38 | Yes | — |
| CNN (No Weather) | 44.78% | 0.230 | N/A | No | — |
| CNN-W (Weather) | 61.73% | 0.650 | N/A | Yes | ✓ Best Overall |
| RNN (No Wx) | 86.06% | N/A | N/A | No | ✓ Count Pred. |
| RNNW (Weather) | ~65% | ~0.66 | N/A | Yes | ✓ Severity |

# 2. Support Vector Machine (SVM vs SVMW)

## 2.1 Overview

Both variants use a LinearSVC + CalibratedClassifierCV pipeline for 7-class fault cause classification. The SVM is the fully optimised model (56 features); SVMW is an unoptimised baseline that adds 11 weather columns but lacks text flags and workshop encoding.

| SVM Accuracy 54.67% | SVMW Accuracy 41.30% | SVM Macro F1 0.488 | SVMW Macro F1 0.28 |
| --- | --- | --- | --- |

## 2.2 Weather Impact Note

Unusually, the non-weather SVM outperforms the weather-enabled SVMW. This is because the SVM pipeline underwent 8 engineering improvements (observation text flags, workshop target encoding, cyclic temporal features, KVA one-hot expansion) while SVMW remains a baseline. Weather features alone cannot compensate for the absence of these high-signal engineered columns — particularly the 14 observation-text binary flags, which are the #1 accuracy driver.

## 2.3 Per-Class Metrics

| Fault Type | SVM Prec. | SVM F1 | SVMW Prec. | SVMW F1 | F1 Δ | Better |
| --- | --- | --- | --- | --- | --- | --- |
| LINE FAULT / LINE SHORT | 0.552 | 0.482 | 0.39 | 0.39 | -0.092 | SVM |
| OVERLOADING | 0.647 | 0.688 | 0.45 | 0.51 | -0.178 | SVM |
| CABLE FAULT / SHORT CIRCUIT | 0.510 | 0.576 | 0.35 | 0.41 | -0.166 | SVM |
| LT SHORT | 0.406 | 0.456 | 0.11 | 0.01 | -0.446 | SVM |
| OTHERS | 0.529 | 0.261 | 0.53 | 0.55 | +0.289 | SVMW |
| OVERHEATED / HT BUSHING DAMAGE | 0.467 | 0.422 | 0.20 | 0.00 | -0.422 | SVM |
| UNBALANCING | 0.551 | 0.532 | 0.22 | 0.11 | -0.422 | SVM |
| MACRO AVG | 0.523 | 0.488 | 0.32 | 0.28 | -0.208 | SVM |

# 3. Artificial Neural Network (ANN — Baseline)

The ANN is a sequential deep neural network (512→256→128→64→39) trained on raw, un-normalised labels. No weather variant was produced for ANN in this study; it serves as a baseline reference and highlights the critical impact of data quality over model complexity.

| Test Accuracy 42.46% | Test Loss 12.15 | Macro Avg F1 0.12 | Weighted Avg F1 0.39 |
| --- | --- | --- | --- |

## 3.1 Architecture Summary

| Layer Stack | Total Parameters | Regularisation |
| --- | --- | --- |
| Dense 512→256→128→64→39 | 187,815 (733 KB) | BatchNorm + Dropout (all layers) |

## 3.2 Key Challenges

- 39 raw classes with near-duplicate labels (e.g. UNBALANCING / UNBalancing / Unbalancing) cause severe label confusion.

- Extreme class imbalance: OVERLOADING has 3,276 samples vs AB CABLE FAULT with only 2.

- Validation accuracy consistently exceeded training accuracy — indicative of stratification mismatch or overly aggressive dropout.

- Best class: CABLE FAULT-SHORT CIRCUIT (F1 0.71); Worst: Line Fault/Line Short (F1 ~0.00) due to duplicate labels.

## 3.3 ANN vs Optimised SVM

| Metric | ANN (Raw Labels) | Optimised SVM |
| --- | --- | --- |
| Test Accuracy | 42.46% | 54.67% |
| Macro Avg F1 | 0.12 | 0.488 |
| Weighted Avg F1 | 0.39 | 0.535 |
| Label Classes | 39 (raw) | 7 (normalised) |
| Feature Count | ~17 | 56 |
| Label Normalisation | No | Yes |
| Class Imbalance Handling | No | Yes (class_weight) |

The SVM outperforms ANN primarily due to data preparation — normalised labels, richer features, and class balancing — not architectural superiority.

# 4. Convolutional Neural Network (CNN vs CNN-W)

Two 1D CNN models were trained to predict fault causes using geographic location hierarchies and Equipment Capacity (kVA). CNN-W additionally incorporates weather condition features. This is the clearest demonstration of weather impact across all experiments.

| CNN Accuracy 44.78% | CNN-W Accuracy 61.73% | CNN Macro F1 0.230 | CNN-W Macro F1 0.650 |
| --- | --- | --- | --- |

## 4.1 Headline Metrics

| Metric | CNN (No Weather) | CNN-W (Weather) | Better |
| --- | --- | --- | --- |
| Overall Accuracy | 44.78% | 61.73% (+16.95 pp) | CNN-W |
| Validation Loss | 1.4244 | 0.8078 (−43%) | CNN-W |
| Macro Avg F1-Score | 0.230 | 0.650 (+0.420) | CNN-W |

## 4.2 Per-Class Fault Metrics

| Fault Type | CNN Prec. | CNN Recall | CNN F1 | CNN-W Prec. | CNN-W Recall | CNN-W F1 | F1 Δ |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Cable Fault / Short Circuit | 0.457 | 0.643 | 0.534 | 0.661 | 0.695 | 0.678 | +0.144 |
| Line Fault / Line Short | 0.429 | 0.364 | 0.394 | 0.676 | 0.333 | 0.446 | +0.052 |
| LT Short Circuit | 0.316 | 0.322 | 0.319 | 0.391 | 0.880 | 0.542 | +0.223 |
| Overloading | 0.499 | 0.686 | 0.577 | 0.687 | 0.644 | 0.665 | +0.088 |

## 4.3 Notable Observations

- LT Short Circuit: CNN-W recall jumps from 0.322 → 0.880 — the largest single improvement across all models and classes.

- Every headline metric improves with weather. CNN-W is unambiguously the better CNN variant.

- Macro F1 nearly tripled (0.230 → 0.650), meaning CNN-W performs far more consistently across all fault classes.

- Validation loss fell 43%, confirming better generalisation — not just training-set overfitting.

# 5. Recurrent Neural Network (RNN vs RNNW)

The RNN experiments differ from others: the non-weather model (RNN) performs regression (predicting daily failure count), while the weather model (RNNW) performs classification into Low / Medium / High severity classes. These are complementary tools rather than direct competitors.

| RNN Accuracy 86.06% | RNN MAE 33.57/day | RNNW Accuracy ~65% | RNNW Macro F1 ~0.66 |
| --- | --- | --- | --- |

## 5.1 Model Setup Comparison

| Dimension | Without Weather (RNN) | With Weather (RNNW) |
| --- | --- | --- |
| Architecture | Bidirectional LSTM | Vanilla RNN |
| Task Type | Failure Count Prediction | Classification (Low/Med/High) |
| Records | 136,344 | 126,777 |
| Input Features | 3 (count, day-of-week, month) | 19 (incl. weather, infra, history) |
| Lookback Window | 7 days | 7 days |

## 5.2 RNNW Per-Class Severity

| Class | Recall | Precision | F1-Score | Count |
| --- | --- | --- | --- | --- |
| Low (0) — Minor faults | ~67.5% | ~70.9% | ~69.1% | 45,558 |
| Medium (1) — Moderate impact | ~58.3% | ~63.7% | ~60.9% | 37,724 |
| High (2) — Critical / Emergency | ~70.2% | ~66.3% | ~68.2% | 43,495 |

## 5.3 When to Use Each RNN Model

| RNN (No Weather) | RNNW (With Weather) |
| --- | --- |
| Scheduling crews & pre-positioning spares | Triaging severity & emergency response planning |
| Volume forecasting — 86.06% accuracy | High class (critical) best predicted — weather signal is strong |
| No weather dependency — simpler, faster to deploy | Requires live weather pipeline for real-time use |

# 6. Weather Impact: Cross-Model Analysis

The table below shows the accuracy delta when switching from a non-weather to a weather-enhanced model for each ML family.

| Model Family | Without Weather | With Weather | Accuracy Δ | Verdict |
| --- | --- | --- | --- | --- |
| SVM | 54.67% (Optimised) | 41.30% (Baseline) | −13.37 pp | No-Wx wins* |
| CNN | 44.78% | 61.73% | +16.95 pp | Weather wins |
| RNN | 86.06% | ~65% | RNN wins (Count) | Complementary |
| ANN | 42.46% (no Wx var.) | — | — | Baseline only |

* SVM inversion explained: The SVMW model is an unoptimised baseline lacking the 14 observation-text flags and workshop target encoding that drive SVM accuracy. Applying the same optimisations to SVMW is projected to add approximately +13 percentage points, pushing it above 54%. The weather features themselves are additive — the deficit is in feature engineering, not weather value.

## 6.1 Key Weather Signals Identified

| Weather Feature | Observed Relationship to Faults |
| --- | --- |
| Temperature (max ≥ 40°C) | Co-occurs with OVERLOADING in summer months — strong predictor for demand surges |
| Humidity (55–70%) | Wet-condition faults (cable, line) trend slightly higher humidity |
| Precipitation | Near-zero for most events; when present, CABLE and LINE faults more likely |
| Heat Index | Temp × Humidity derived feature — captures compound thermal stress on transformers |
| Extreme Heat Flag | Binary flag for max temp ≥ 40°C — top engineered weather signal |

# 7. Recommendations & Next Steps

## 7.1 Immediate Actions

- Deploy CNN-W as the primary fault cause classifier — it achieves 61.73% accuracy and macro F1 of 0.650, the best overall classification performance.

- Apply the same 8 optimisations from SVM to the SVMW baseline: text flags, workshop encoding, cyclic temporal features, KVA one-hot expansion.

- Normalise ANN labels from 39 raw classes to 7–10 canonical classes to unlock the ANN's representational capacity.

- Maintain a reliable real-time weather data pipeline — CNN-W and RNNW performance is directly dependent on input quality.

## 7.2 Model Deployment Strategy

| Use Case | Recommended Model | Rationale |
| --- | --- | --- |
| Fault cause classification (real-time) | CNN-W | Best accuracy & F1; weather data available |
| Fault cause classification (no weather) | Optimised SVM | 54.67% without weather dependency |
| Daily failure volume forecasting | RNN | 86.06% accuracy; simple 3-feature pipeline |
| Emergency severity triage | RNNW | Low/Med/High with 65% accuracy; weather-enhanced |

## 7.3 Future Work

- Train an ANN-W (ANN with weather) after label normalisation to complete the weather-impact comparison matrix.

- Standardise reporting across all model evaluations: consistent fault category labels, weighted average metrics, and identical test splits.

- Investigate fault categories present in non-weather models but absent in weather-enhanced variants (LT Line Fault, Unbalancing, Others) — document consolidation rationale.

- Evaluate ensemble approaches: combining CNN-W predictions with RNNW severity scores for a unified fault assessment pipeline.

- Introduce SMOTE or class_weight balancing to ANN and CNN models to address the significant class imbalance remaining in both architectures.

Report compiled from: ANN_Power_Failure_Report | CNN_Comparison_Report_v2 | SVM_vs_SVMW_Comparison | RNN_vs_RNNW_Comparison

Uttar Pradesh Power Distribution Grid | Predictive Fault Maintenance | ML Comparison Study